## Slide 1: Generator and ATS
Ronald Slutter

## Slide 2: Generator and ATS Contents
Typical Generator and Automatic Transfer Switch (ATS) Single Lines
Manual Transfer Switch (MTS) and Portable Generator Connections
Standard Vs. Bypass Isolation
Open, Closed and Delayed Transition ATS
Contactor Vs. Circuit Breaker Based Designs
When 4 Pole ATS is required
Generator Sub-base Tank Fuel Polishing

## Slide 3: Typical Generator and Automatic Transfer Switch (ATS) Single Lines

## Slide 4: Typical Single Generator and ATS
Represents the typical configuration.

## Slide 5: Typical Dual Generator and ATS
Represents the most typical configuration with 2 generators and 2 ATS.

## Slide 6: Manual Transfer Switch (MTS) and Portable Generator Connections

## Slide 7: Portable Generator Connection Cabinet
Typically used to transfer power from portable generator to ATS. Allows very quick transfer from fixed generator to portable generator.
Typically connected to portable generator connection cabinet.
3 Pole or 4 Pole.
On – Off - On.

## Slide 8: Portable Generator Connection Cabinet
Typically used to connect temporary cables from portable generator to MTS.
Provides power and controls for portable generator.

## Slide 9: Triple Breaker Docking Station
Provides integrated connection for load bank and portable generator:
Phase rotation monitor
All aluminum NEMA 3R or stainless 4X construction
Patented tamper-resistant rake system to prevent cable theft and unauthorized disconnection
CamLok connections compatible with any rental generator or load bank for facility backup and permanent generator testing
Mechanical or Kirk Key interlock to safely disconnect and transfer power

## Slide 10: Standard Vs. Bypass Isolation

## Slide 11: ATS Standard
ATS mechanism does not have a bypass feature.

## Slide 12: ATS Bypass Isolation
ATS mechanism has a bypass feature.

## Slide 13: Open, Closed and Delayed Transition ATS

## Slide 14: ATS Open Transition Standard
Open transition – Break Before Make
Not recommended but sometimes used – Creates a transient surge to the load.

## Slide 15: ATS Delayed Transition Standard
Delayed Transition – Center Off
Often used – 5 second delay recommended. No Transient to the load

## Slide 16: ATS Closed Transition Standard
Closed Transition – Make Before Break
Used with Utility Approval. Requires Advanced configuration.

## Slide 17: ATS Open Transition Bypass Isolation
Open transition – Break Before Make
Not recommended but sometimes used – Creates a transient surge to the load.

## Slide 18: ATS Delayed Transition Bypass Isolation
Delayed Transition – Center Off
Often used – 5 second delay recommended. No Transient to the load

## Slide 19: ATS Closed Transition Bypass Isolation
Closed Transition – Make Before Break
Used with Utility Approval. Requires Advanced configuration.

## Slide 20: Contactor Vs. Circuit Breaker Based Designs

## Slide 21: Basic Contactor ATS Design
Typical contactor-based ATS switch design.
Rating contacts 200,000 cycles lifetime.

## Slide 22: Basic Circuit Breaker ATS Design
Typical contactor-based ATS switch design.
Rating of Circuit Breaker Approx 300 Cycles per year.

## Slide 23: Basic Switchgear Circuit Breaker Design
Typical electrically operated circuit breaker based transfer switch design with HMI.

## Slide 24: When 4 Pole ATS is required

## Slide 25: NEC 230.95 Ground Fault Protection
Ground-fault protection of equipment shall be provided for solidly grounded wye electric services of more than 150 volts to ground but not exceeding 1000 volts phase-to-phase for each service disconnect rated 1000 amperes or more.

## Slide 26: NEC 230.95 Performance Testing
The ground-fault protection system shall be performance tested when first installed on site.
This testing shall be conducted by a qualified person(s) using a test process of primary current injection, in accordance with instructions that shall be provided with the equipment.

## Slide 27: 3 Pole Solidly Grounded System

## Slide 28: 4 Pole Solidly Grounded System

## Slide 29: 3 Pole vs. 4 Pole Bonding Separately Derived Systems

## Slide 30: Generator Sub-base Tank Fuel Polishing

## Slide 31: Sampling a Fuel Tank

## Slide 32: Generator Diesel Fuel Polishing

## Slide 33: Two Content Layout with SmartArt
First bullet point here
Second bullet point here
Third bullet point here
First bullet point here
Second bullet point here
Third bullet point here

## Slide 34: Add a Slide Title - 2

## Slide 35: Add a Slide Title - 3

## Slide 37: Add a Slide Title - 4

## Slide 38: Add a Slide Title - 5